Add Company Logo

Quality GUIDELINES

Key quality guidelines for Air Conditioning Maintenance

(Company Name)

Date:

Author:

Table of Contents

1.	INTRODUCTION	2

1.1.	Company Vision and Services Offered	2

1.2.	Scope of This Guideline	2

2.	QUALITY MANAGEMENT SYSTEM	3

2.1.	General Requirements	3

2.2.	Control of Documents	3

3.	MANAGEMENT RESPONSIBILITY	4

3.1.	Management Commitment	4

3.2.	Quality Objectives and Quality Management Planning	4

4.	RESOURCE MANAGEMENT	5

4.1.	Human resources management	5

4.2.	Information technology management	5

4.3.	Tolling and Infrastructure management	6

4.4.	Financial management	6

5.	BUSINESS CAPTURING AND BIDDING	6

5.1.	Customer’s Requirements and Service Planning	6

5.2.	Bid Preparation and Submission	7

5.3.	Bid acceptance and hiring	8

6.	MAINTENANCE SERVICES	8

6.1.	Preparation and Execution Planning	8

6.2.	Materials and Supplies Purchasing	8

6.3.	Tooling and Equipment	8

6.4.	Customer Property	9

6.5.	HVAC Maintenance	9

7.	MEASUREMENT, ANALYSIS AND IMPROVEMENT	10

7.1.	Customer Feedback	10

7.2.	Internal Audit	11

7.3.	Performance Monitoring	11

7.4.	Continuous Improvement	11

8.	APPENDIX: HVAC Maintenance Checklists	13

8.1.	Air Distribution Inspection Checklist	13

8.2.	Steam Distribution System Inspection Checklist	13

8.3.	Controls and Safety Systems Inspection Checklist	14

8.4.	Gas Furnace System Inspection Checklist	14

8.5.	Oil Furnace Inspection Checklist	17

8.6.	Electric Furnace Inspection Checklist	19

8.7.	Evaporator Coil inspection checklist	20

8.8.	Condenser Unit Inspection Checklist	21

8.9.	Fan Coil Inspection Checklist	22

8.10.	Gas Boiler System Inspection Checklist	24

8.11.	Oil Boiler System Inspection Checklist	26

8.12.	Electric Boiler System Inspection Checklist	28

8.13.	Package Units	29

8.14.	Geothermal/ Water Source Heat Pumps	32

8.15.	Evaporative Coolers	32

8.16.	Accessories	33

9.	APPENDIX: Customer feedback tool	36

# INTRODUCTION

This quality guideline documents the commitment of the company to maintain a high-level of service quality and strong customer service, and fosters continual improvement.

Quality is an integral part of the entire business operation, hereafter this quality guideline will provide information on the key elements of the quality system, guidelines on how to deliver our service, how to manage resource to achieve the required standards, and how to collect customer feedback and use them to improve the service delivery.

# Company Vision and Services Offered

Our company provides heating, ventilating, and air conditioning (HVAC) maintenance services for residential and retail

Our company aims to (Vision)

# Scope of This Guideline

Our commitment to quality in work practice and customer service is defined through our main processes. This guideline aims at:

- demonstrating our ability to consistently provide quality service that meets customer and applicable regulatory requirements,

- addressing customer satisfaction through the effective application of our quality standards, including processes for continual improvement and the prevention of nonconformity,

- managing effectively and efficiently our employees and technical resources to deliver superior performance, and

- managing customer feedback to continuously improve our performance.

This guideline is available for inspection by our customers, potential customers, third party quality auditors, and regulatory agencies.

The scope of the quality guideline is specifically defined as everything within the direct control and authority of the top management and its shareholders only. Many functions may be performed by other parties, and those are treated as customers and/or suppliers, as appropriate.

The quality guideline is maintained as a read-only document and is available to all employees and to other interested and authorized parties. All copies printed are reference copies and are uncontrolled.

The quality guideline will be reviewed by the management and revised as required. After management review, the quality guideline is updated (if needed) by incorporating all approved changes. The management may approve minor changes and updates. The revision date is updated, and the document is re-approved and released as a new issue in its entirety. The revision data on the cover refers to the entire document.

# QUALITY MANAGEMENT SYSTEM

# General Requirements

Our company has established, documented and implements an effective quality system as a means of ensuring that its services conform to specified requirements, to foster an environment of continual improvement with an eventual goal of achieving quality excellency.

The core processes describe all the processes that are necessary to realize and deliver the desired service to its customers. The core processes are

- Marketing and sales

- Business capturing and bidding

- Maintenance services

- Measurement, analysis and improvements

Our Support Processes describe all other business requirements that are necessary to manage and control resources, and to conduct business in an orderly manner. The main processes are:

- Human resources management

- Finance and accounting management

- Technology, infrastructure and tooling management

- Quality management

The sequence and interaction of the Core and Support Business Processes are described in the following paragraphs.

# Control of Documents

We ensure that documents and data that relate to our service are controlled. This control also extends to documents of external origin that are maintained solely by us, such as performance standards, and service specifications.

All electronic quality guidelines are stored.

A list of technical documents, identifying the current revision status of each, is established and is readily available.

All personnel are required to identify required changes in documents and are encouraged to suggest improvements.

After a revision issue, obsolete hard copy documents are promptly removed from points of use. The obsolete master document is archived and may be retained for knowledge preservation purposes.

We maintain quality records to demonstrate conformance to specified requirements. Control provides for the identification, collection, indexing, filing, access, storage, maintenance, and disposition of quality records. Pertinent customer or supplier records are also maintained and controlled.

# MANAGEMENT RESPONSIBILITY

# Management Commitment

The management is committed to the development and improvement of effective quality guidelines. This commitment is demonstrated by:

- Communicating to the organization the importance of meeting all customer, regulatory, and legal requirements.

- Quality objectives and guidelines are published and displayed across our office

- Quality reviews and in particular by reviewing customer feedbacks

The management ensures that customer needs and expectations are determined, converted into requirements, and fulfilled with the aim of meeting or exceeding those expectations. The specific needs of our customers are determined through verbal and written communications.

# Quality Objectives and Quality Management Planning

The quality objectives of our company can be summarize as it follows:

- Ensure high reliable and satisfactory service to our customers

- Apply our quality guidelines to our work activities

- Improve our people and processes to anticipate, meet, and exceed the needs of our customers.

- Support the continuous  improvement of the quality of our services

Our objectives have been communicated to all employees.

Our management has identified and planned the resources needed to achieve its quality objectives. The quality plan identifies the core and support business processes. The quality plan describes the overall plan for quality assurance. The quality plan consists of business and support processes and responsibilities. The key processes are illustrated in the below table.

| # | Business Process | Responsible Person |
| --- | --- | --- |
| 1 | Marketing and sales | Text |
| 2 | Business capturing and bidding | Text |
| 3 | Maintenance services | Text |
| 4 | Measurement, analysis and improvements | Text |
| 5 | Human resources management | Text |
| 6 | Finance and accounting management | Text |
| 7 | Technology, infrastructure and tooling management | Text |
| 8 | Quality management | Text |

Our management ensures that communication about those processes is maintained across the organization and our people.

Our management conducts periodic review of our processes to continuously improve performance and customer services. Results of those reviews are recorded.

# RESOURCE MANAGEMENT

Our company needs to manage essentially four different types of resources: our people, information technology, the tooling and infrastructure required to deliver our service, and financials.

# Human resources management

Personnel performing specific tasks are qualified on the basis of appropriate education, training, observed skills, and experience, as required. All technicians/professionals are evaluated as fully competent in a specific job before being allowed to work independently.

A training plan is prepared and scheduled annually. Training is provided either on or off the job, internally or externally, as appropriate. We ensure that its personnel are aware of the relevance and importance of their jobs and how they contribute to the achievement of the quality objectives.

The key HR activities done by the management are

- Maintain database of human resources with key personal information

  - Name

  - Date of Birth

  - Passport number and expiration date

  - IKAMA number

  - Start of employment

  - Title/Role

  - Skills

  - Certification / Qualification

  - Education

  - Training performed

  - Other

- Maintain database of potential recruitment agencies and candidates

- Maintain training plan and service providers

  - Training course

  - Skill development

  - Duration of the training

  - List of potential training provider

  - Cost of training

# Information technology management

Our company has the required information technology infrastructure to support our business. We maintain

- A digital presence with all information on our business (e.g., website, registration on google+, registration on digital directories, etc)

- Accounting system to keep track of our revenues, costs, jobs, inventories

- Microsoft office tools ( or other) for all office activities

- Specific software to test our tooling and equipments

- PCs for our offices

- Online storage for all our documents, invoices, bids, etc

We maintain the licenses of all software applications.

# Tolling and Infrastructure management

Tooling and infrastructure required to perform our maintenance services are identified by the management and maintained properly

All our equipment, tooling and infrastructure are recorded in a database and maintained by the management.

The tooling database will have the following information

- Tool name

- ID number

- Cost

- Calibration/certification (if required)

- Last maintenance / test

# Financial management

We maintain records of our financials and periodically we monitor the financial performance of our business.

We use an external accountant to prepare our annual financial reports, including profit and loss, balance sheet, and cash flow.

In particular we conduct the following activities

- Prepare, issues and store invoices

- Receive, pay and store receipts

- Track inventory level

- Track cash position on the bank account

- Issue salary slips on monthly basis

- Monitor credit line and debt position

- Pay taxes

- Report all transactions on the company accounting system

- Extract on quarterly basis the bank transactions

On annual basis, engage accountant and conduct the following activities

- Provide all data and bank transactions

- Review the reports provided by the accounting team

- Approve the financial report

# BUSINESS CAPTURING AND BIDDING

# Customer’s Requirements and Service Planning

Upon receipt of new service requirements, we plan the sequence of steps required to realize the specified customer’s requirements.

- Determination of customer’s requirements include the following steps

- Collect customer’s requirements and data on the HVAC system;

- Understand the required tools and material for service delivery, with associated costs;

- Understand location, travel requirements and time for service delivery;

- Understand any obligations related to the contract, including regulatory and legal requirements.

- Ensure requirements are adequately defined and documented.

- Ensure differences between the standard requirements and those in the request are identified, and communicated to the customer

- Key questions to ask to the client

- If the first time, understand the home history (when built, renovations, etc.)

- Identify the HVAC system, components, and accessories:

  - Equipment Type

  - Brand and model

  - Serial number if applicable

  - Year of manufacture

  - Start-up date

  - Last time of a repair or scheduled maintenance

  - Any previous faults or problems

- Planning of the service delivery consists of the following steps

- Ensure that customer requirements are fully understood and we have the capability to meet them.

- Identify minimum equipment performance criteria

- Identify appropriate checklists for each piece of equipment in the inventory

- Identify technical documentation are required for the specific service

- Identify and prepare all tooling required

- Identify the manpower requirements

- Identify and plan the material required

- Identify quality records that are necessary to provide conformity of the results.

# Bid Preparation and Submission

Once customer requirements have been understood and assessed, we will prepare a bid with

- a clear definition of our scope of work,

- description of the materials required,

- time requirements to deliver the service

- the name of our representative that will deliver the service

- the cost of our service

- time of delivery

The bid will be proper document and reviewed for quality purpose. Once the bid is ready, we will submit our proposal to our customer by using digital or traditional mail.

# Bid acceptance and hiring

Once bid has been submitted, we ensure that our bid is accepted by the client and a formal engagement is signed by both parties. The engagement letter should include some basic information

- Scope of work

- Material provided

- Start of the work and expected duration

- Assigned employee

- Cost and Taxes ( if applicable)

- Key terms and conditions

Once the engagement letter (e.g., hard copy or electronically) is confirmed by both parties, the management launch the execution planning

# MAINTENANCE SERVICES

# Preparation and Execution Planning

The job preparation and execution planning consists mainly of the following activities

- Inform technicians on the scope of work and plan resources

- Handle and prepare materials

- Handle and prepare tools and equipment

- Prepare checklists for the work

- Engage the customer to confirm the meeting

# Materials and Supplies Purchasing

Materials, supplies, and services from other companies may be required to perform HVAC maintenance.  When purchasing materials and supplies we will conduct the following tasks

- Ensure that purchased materials and services conform to specification and are purchased from approved sources

- Ensure that the purchased material and supplies have the required technical documentation

- Ensure that incoming material is not used or processed until it has been inspected or otherwise verified to specified requirements

- Maintain a list of active suppliers and the materials or services they provide

Verification of purchased product or service by the Customer may be required. Once the customer ask for verification of our products, we will provide all technical and commercial documentation. However, this does not absolve our responsibility to provide acceptable product, nor will it preclude subsequent rejection by the customer.

# Tooling and Equipment

We ensure that equipment and tools are adequately identified and tested before the use.

- Identification - Equipment is adequately identified through all stages by means of an ID number.

- Maintenance - Where applicable, we ensure that our tools and devices:

  - are maintained on a defined periodic basis, against devises standards;

  - are protected from damage and deterioration during handling, maintenance, and storage;

  - maintenance results are recorded;

- Inspection and Test Status - We ensure that our tools and equipment are inspected and testes, and the status is maintained to ensure that only equipment that has passed required inspections, tests, and calibration are dispatched or used as serviceable items.

# Customer Property

We exercise care with any customer property while it is under our control or being used by our company. We identify, verify, protect, and maintain customer property provided for service. Any occurrence of customer property that is lost, damaged, or otherwise found to be unsuitable for use is recorded and reported to the customer.

# HVAC Maintenance

A maintenance inspection seeks to identify deficiencies that degrade or impair the HVAC system. Our responsibilities, as a maintenance contractor, consists of

- Inspect all HVAC equipment and components to identify faults which contravene manufacturer’s guidelines, customer’s safety or health, any other regulations and industry standards

- Inform the customer of improper operation finding, corrective action taken, and the cost

- If during the maintenance, it is determined that there is a condition that could result in unsafe operation, we will shut off the HVAC system and advise the client in writing, of the unsafe condition

Our maintenance activities are conducted by following specific checklists, and are structured along the following main activities:

- Inspection tasks: This portion of the checklist describes the minimum tasks that are required for most major pieces of residential equipment

- Recommended corrective actions: The checklists offer remedies for faults identified during the inspection process. All corrective actions are performed in accordance with the applicable OEM’s instructions.

- Component maintenance: The major pieces of HVAC equipment and accessories have checklists. If the HVAC system in the home is not covered by a checklist, we will assemble a checklist from similar functions listed on checklists

- Inspection Task scheduling: Inspection tasks for cooling and heating shall be performed when the equipment is operating within the temperature parameters established by conditions which meet the manufacturer’s operating range. We shall have the discretion to increase inspection tasks or frequency of inspection to address deficiencies if unacceptable performance is found during successive inspections.

This checklists are assembled based on the US HVAC Association

| # |  | Component / Equipment | Description | Checklist |
| --- | --- | --- | --- | --- |
| 1 | Air Distribution |  | Plenums, trunk ducts, fittings, branch ducts, boots, grilles, registers and diffusers | 8.1 |
| 2 | Steam Distribution System |  | Piping, radiator, controls, steam traps. | 8.2 |
| 3 | Controls and Safety Systems |  | Thermostats, outdoor sensors, humidistats, zone controls | 8.3 |
| 4 | Furnace |  | Gas-fired air heating system | 8.4 |
|  |  |  | Oil-fired air heating system | 8.5 |
|  |  |  | Electric air heating system | 8.6 |
| 5 | Evaporator Coil |  | The cased or field enclosed evaporator coil, metering device, condensate drain, and associated refrigeration tubing | 8.7 |
| 6 | Condenser Unit |  | The outdoor section of a split system: air conditioner or heat pump | 8.8 |
| 7 | Fan Coil |  | The filter rack, evaporator coil, metering device, associated refrigeration tubing, blower assembly, condensate drain, and electric auxiliary heat | 8.9 |
| 8 | Boiler |  | Gas-fired water heating system | 8.10 |
|  |  |  | Oil-fired water heating system | 8.11 |
|  |  |  | Electric water heating system | 8.12 |
| 9 | Package Units |  | Packaged air conditioners or heat pumps | 8.13 |
| 10 | Geothermal/ Water Source Heat Pumps |  | Packaged geothermal/water source heat pump units | 8.14 |
| 11 | Evaporative Coolers |  | Packaged cooling only equipment using evaporative heat transfer | 8.15 |
| 12 | Accessories |  | Heat and energy recovery ventilators, central system humidifiers, central system dehumidifiers, electronic air cleaners, media air cleaners, ultra-violet lights, economizers, and condensate pumps | 8.16 |

# MEASUREMENT, ANALYSIS AND IMPROVEMENT

We define, plan, and implement the monitoring activities needed to ensure conformity and achieve quality improvement.

# Customer Feedback

We monitor information on customer satisfaction as one of the measurements of our service delivery. We conduct the following activities

- Ask to the customer feedback on the performed job

- Collect customer feedback from other sources ( google+ and other platfomrs)

- Store customer feedback in a customer feedback database

- Review customers’ feedback, and identify potential improvement opportunities.

- Introduce the improvement in the our current business processes

- Update the quality guideline and checklist

# Internal Audit

We conduct annual audits. The purpose of the internal audit is to determine whether:

- Our service conforms to the requirements of the quality guidelines;

- Our quality guidelines are being effectively implemented and maintained.

Or quality audit are performed in accordance of the following guidelines

- Internal quality audits are planned and scheduled at least on annual basis

- Trained personnel independent of those having direct responsibility for the activity being audited carry out the audits.

- The results of the internal audits are documented and brought to the attention of the personnel.

- The corrective action are identified and submitted for management review.

- Management introduces the corrective action found during the audit.

- Subsequent audits verify the effectiveness of the corrective actions taken.

# Performance Monitoring

We monitor the performance of our maintenance services by using a set of key indicators. Those indicators are monitored on periodic basis

| # | KPIs | Formula / Description | Frequency |
| --- | --- | --- | --- |
| 1 | Revenues growth to measure sales performance | (Revenue Year 1 / revenues year 2) -1 | Annual |
| 2 | Profitability | (Total revenues – Total Costs)/Total revenues | Annual |
| 3 | Revenues per employee | Total revenues / total employee | Annual |
| 4 | Customer satisfaction | Total satisfactory work / total jobs per month | Monthly |
| 5 | Total returning customers | New customers / total customers | Annual |
| 6 | Average time to complete a job | Total working time on the job/ number of jobs | Monthly |
| 7 | People development | Total days of training / total number of people | Annual |

Based on the KPIs assessment, we identified areas of focus to improve our service delivery and quality.

# Continuous Improvement

The continuous improvement process is based the analysis of the customer feedback, results of the audit, corrective and preventive actions.

We take corrective action to eliminate the cause of identified nonconformities in order to prevent recurrence. The corrective actions are introduced according to the following steps:

- identifying nonconformities (including customer complaints);

- determining the causes of nonconformity;

- evaluating of the need for actions to ensure that nonconformities do not recur;

- determining and implementing the corrective actions needed;

- recording results of action taken;

- reviewing and evaluation of corrective action taken to assess its effectiveness.

We take preventive actions to eliminate the causes of identified potential nonconformities to prevent initial occurrence. The preventive actions are introduced according to the following steps:

- identification of potential nonconformities and their causes;

- determination of the steps needed to eliminate identified causes and completion of the preventive action implementation;

- recording results of action taken;

- review and evaluation of preventive action taken to assess its effectiveness;

- ensuring that relevant information on actions taken, including changes to procedures, is subject to management review.

# APPENDIX: HVAC Maintenance Checklists

# Air Distribution Inspection Checklist

| # | Inspection Task | Recommended Corrective Actions |
| --- | --- | --- |
| 1 | Inspect for particulate accumulation on filters. | Clean or replace filters if accumulation results in PD higher than design or if airflow is outside of established operating limits. |
| 2 | Inspect air filter housing integrity and air seal. | Correct as needed. |
| 3 | Inspect grilles, registers, diffusers, and trunk/branch balancing dampers for dirt accumulation. | Clean as needed. |
| 4 | Inspect all accessible ductwork for areas of moisture accumulation or biological growth. | Install access doors as needed. Clean or replace as needed. |
| 5 | Inspect integrity of all accessible ductwork insulation. | Repair ductwork insulation and associated exterior vapor retarders and repair all accessible rips, voids to insulation adhesives and/or tapes. |
| 6 | Inspect the integrity of all accessible ductwork including: duct strapping, hangers, sections, joints, and seams. | Note improper alterations, straps, air leaks, and failing duct tapes or mastics. Repair, seal, replace as necessary. |
| Closure of the job |  |  |
| 7 | Clean the workspace Collect all tools and material | Not applicable |
| 8 | Ask feedback on the job to the customer Report the feedback in the customer feedback tool | Not applicable |

# Steam Distribution System Inspection Checklist

| # | Inspection Task |  | Recommended Corrective Actions |
| --- | --- | --- | --- |
| 1 |  | Inspect safety devices. | Correct or replace as needed per manufacturer’s recommendations. |
| 2 |  | Inspect piping for leaks. | Repair as needed. |
| 3 |  | Inspect piping anchors/supports for integrity and inspect piping for alignment and expansion fittings for proper operation. | Repair as needed. |
| 4 |  | Inspect blowdown or drain valve. | Clear all debris to ensure proper operation. Replace as needed. |
| 5 |  | Inspect system steam traps, pumps, and controls. | Clean or replace as needed to ensure proper operation |
| 6 |  | Inspect for evidence of buildup or fouling on heat exchange surfaces. | Restore as needed to ensure proper operation. |
| 7 |  | Inspect for proper fluid flow. | Clean, adjust, and repair as needed to restore proper flow (e.g., drain the boiler annually). |
| 8 |  | Inspect strainers. | Clean as needed. |
| 9 |  | Visually inspect external piping insulation and vapor barrier for integrity. | Repair or replace as needed. |
| 10 |  | Inspect radiator inlet valve and vents. | Open valve and adjust vents as needed. |
| Closure of the job |  |  |  |
| 16 |  | Clean the workspace Collect all tools and material | Not applicable |
| 17 |  | Ask feedback on the job to the customer Report the feedback in the customer feedback tool | Not applicable |

# Controls and Safety Systems Inspection Checklist

| # | Inspection Task | Recommended Corrective Actions |
| --- | --- | --- |
| 1 | Test modes of operation and control sequences. Test system control devices to ensure they are maintaining their expected range. | Repair or replace controls as needed to ensure proper operation. |
| 2 | Test zoning control’s modes of operation, zone control to ensure proper damper/valve operation and test bypass dampers for proper function. | Repair or replace components as needed to ensure proper operation. |
| 3 | Test remote control thermostat in all modes of operation. | Replace battery annually, check for corrosion on the battery contact points. |
| 4 | Initiate a test of the defrost control boards mode of operation, for those with that capability. | Repair, replace or adjust controls as needed. |
| 5 | Test drain pan safety switch(es) for proper operation. | Repair wiring or replace safety switch as needed. |
| 6 | Test unit safety switches3. | Repair wiring or replace safety switch as needed. |
| 7 | Verify that all selectable pins, jumpers, and/or dip switch positions on control board are correctly positioned for the application. | Use OEM’s installation and/or technical publications for guidance on proper settings. |
| Closure of the job |  |  |
| 8 | Clean the workspace Collect all tools and material | Not applicable |
| 9 | Ask feedback on the job to the customer Report the feedback in the customer feedback tool | Not applicable |

# Gas Furnace System Inspection Checklist

| # | Inspection Task | Recommended Corrective Actions |
| --- | --- | --- |
| Cabinet |  |  |
| 1 | Inspect cabinet, cabinet fasteners, and cabinet panels. | Repair or replace insulation to ensure proper operation. Replace lost fasteners as needed to ensure proper integrity and of equipment (as applicable). Seal air leaks. |
| 2 | Inspect the required clearance (e.g., combustion and service) around cabinet. | Record and report instances where the cabinet does not meet requirements. |
| Electrical |  |  |
| 3 | Inspect electrical disconnect box. | Ensure electrical connections are clean and tight. Ensure fused disconnects use the proper fuse size and are not bypassed. Ensure case is intact and complete. Replace as necessary. |
| 4 | Ensure proper equipment grounding. | Tighten, correct and repair as necessary. |
| 5 | Measure and record line voltage. | Compare to OEM specifications or equipment nameplate data. Notify homeowner and/or utility. |
| 6 | Inspect and test contactors and relays. | Look for pitting or other signs of damage. Replace contactors and relays demonstrating evidence of excessive contact arcing and pitting. |
| 7 | Inspect electrical connections and wire. | Ensure wire size and type match the load conditions. Tighten all loose connections, replace heat discolored connections, and repair or replace any damaged electrical wiring. |
| 8 | Inspect motor capacitors. | Replace those that are bulged, split, incorrectly sized, or do not meet OEM specifications. |
| 9 | Measure and record amperage draw to motor/nameplate data (FLA) as available. | If outside OEM rating or specification, inspect for cause and repair as necessary. |
| Blower Assembly |  |  |
| 10 | Determine and record airflow across heat exchanger. | Verify all grilles, registers, and balancing dampers are open and free of obstruction and operating properly. Adjust, clean, replace, and repair as necessary to ensure to proper airflow. |
| 11 | Test variable frequency drive (e.g., ECM) for proper operation. | Replace if necessary to ensure proper operation. |
| 12 | Inspect fan belt tension. Inspect belt and pulleys for wear and tear. | Repair or replace as necessary to ensure proper operation (if applicable). |
| 12 | Confirm the fan blade or blower wheel has a tight connection to the blower motor shaft. Inspect fan for free rotation and minimal endplay. Measure and record amp draw. | Lubricate bearings as needed, only if recommended by OEM. If amp draw exceeds OEM specifications then adjust motor speed or otherwise remedy the cause. If due to motor failure recommend replacement of blower motor. |
| Condensate Removal |  |  |
| 13 | Inspect condensate drain piping (and traps) for proper operation. | Clean, insulate, repair, or replace as necessary. |
| Gas Combustion |  |  |
| 14 | Inspect burner and flue for signs of water, corrosion, and blockage. | Identify cause and clean, repair, or replace as necessary. |
| 15 | Test inducer fan motor and blower assembly. | Correct as needed. |
| 16 | Inspect heat exchanger for signs of corrosion, fouling, structural problems (e.g., cracks, perforations, and bulges), and erratic flame operation during blower operation. | Identify cause and clean, repair, or replace as necessary. |
| 17 | Visually inspect burners for signs of contamination. | Clean, repair or replace as necessary. |
| 18 | Inspect the burner blower wheel | Clean as needed to ensure proper operation. |
| 19 | Inspect hot surface igniter for cracks (white spots when energized or check cold with ohmmeter and proper supply voltage). | Replace if outside OEM’s specifications. |
| 20 | Measure and record inlet gas pressure at inlet pressure tap. | If the inlet gas pressure is insufficient for OEM operation specifications, contact the gas supplier. |
| 21 | Measure, record, and adjust manifold pressure as necessary. | Adjust the gas valve to provide proper manifold pressure. |
| 22 | Inspect ceramic insulator, flame probe, and associated wiring for any cracks or abnormalities. | Clean according to OEM recommended procedures. Replace as needed. |
| 23 | Test main burner ignition sequence and flame safety; verify proper operation. | Record micro-amps for comparison with OEM specifications. If outside of OEM operational range, correct combustion problem or replace components as needed. |
| 24 | Test burners. | Fire unit and adjust air shutters (if used) for OEM specification compliance. |
| 25 | Inspect the spark igniter and associated wiring. Verify that spark gap complies with OEM specifications. | If cracking of ceramic insulator or deterioration of spark electrodes is noted, igniter assembly shall be replaced. If cracking or deterioration of ignition wiring is observed, wiring shall be replaced. |
| 26 | Test inducer fan motor and blower assembly. | Correct as needed. |
| 27 | Ensure combustion air volume or provision is correct. | Ensure air volume is correct per OEM instructions and local code. |
| 28 | Perform combustion analysis test. Measure and record test results. | Adjust as needed. |
| 29 | Measure and record TD across the heat exchanger. | If TD is outside OEM’s specifications, identify cause and then clean, repair, or replace as necessary. |
| Venting |  |  |
| 30 | Inspect vent exhaust system (e.g., chimney, chimney liner, flue, inlet and exhaust vent) for signs of improper condensation, water corrosion, cracks, fractures, and blockages. | Clean, remove blockages, repair, or replace as necessary. |
| 31 | Inspect all vent connectors for rust discoloration, or signs of condensate. | Ensure they are securely fastened. Repair or replace as necessary. |
| 32 | Inspect inlet and exhaust vent pipe for proper support, slope, and termination. | Repair or replace as necessary. |
| 33 | Inspect for combustible materials placed too close to vent or pipe. | Relocate to safe place or provide approved clearance reduction. |
| Closure of the Job |  |  |
| 34 | Clean the workspace Collect all tools and material | Not applicable |
| 35 | Ask feedback on the job to the customer Report the feedback in the customer feedback tool | Not applicable |

# Oil Furnace Inspection Checklist

| # |  | Inspection Task | Recommended Corrective Actions |
| --- | --- | --- | --- |
| Cabinet |  |  |  |
| 1 | Inspect cabinet, cabinet fasteners, and cabinet panels. |  | Repair or replace insulation to ensure proper operation. Replace lost fasteners as needed to ensure proper integrity and fit/finish of equipment (as applicable). Seal air leaks. |
| 2 | Inspect the required clearance (e.g., combustion and service) around cabinet. |  | Record and report instances where the cabinet does not meet the requirements. |
| Electrical |  |  |  |
| 3 | Inspect electrical disconnect box. |  | Ensure electrical connections are clean and tight. Ensure fused disconnects use the proper fuse size and are not bypassed. Ensure case is intact and complete. Replace as necessary. |
| 4 | Ensure proper equipment grounding. |  | Tighten, correct and repair as necessary. |
| 5 | Measure and record line voltage. |  | Compare to OEM specifications or equipment nameplate data. Notify homeowner and/or utility. |
| 6 | Inspect and test contactors and relays. |  | Look for pitting or other signs of damage. Replace contactors and relays demonstrating evidence of excessive contact arcing and pitting. |
| 7 | Inspect electrical connections and wire. |  | Ensure wire size and type match the load conditions. Tighten all loose connections, replace heat discolored connections, and repair or replace any damaged electrical wiring. |
| 8 | Inspect motor capacitors. |  | Replace those that are bulged, split, incorrectly sized, or do not meet OEM specifications. |
| 9 | Measure and record amperage draw to motor/nameplate data (FLA) as available. |  | If outside OEM rating or specification, inspect for cause and repair as necessary. |
| Blower Assembly |  |  |  |
| 10 | Determine and record airflow across heat exchanger. |  | Verify all grilles, registers, and balancing dampers are open and free of obstruction and operating properly. Adjust, clean, replace, and repair as necessary to ensure to proper airflow. |
| 11 | Test variable frequency drive (e.g., ECM) for proper operation. |  | Replace if necessary to ensure proper operation. |
| 12 | Inspect fan belt tension. Inspect belt and pulleys for wear and tear. |  | Repair or replace as necessary to ensure proper operation (if applicable). |
| 13 | Confirm the fan blade or blower wheel has a tight connection to the blower motor shaft. Inspect fan for free rotation and minimal endplay. Measure and record amp draw. |  | Lubricate bearings as needed, only if recommended by OEM. If amp draw exceeds OEM specifications then adjust motor speed or otherwise remedy the cause. If due to motor failure recommend replacement of blower motor. |
| Oil Combustion |  |  |  |
| 14 | Inspect combustion chamber for structural problems (e.g., cracks, perforations, and deformities). |  | Identify cause and clean, repair, or replace as necessary. |
| 15 | Inspect heat exchanger and internal flue for signs of corrosion, fouling, and erratic flame operation during blower operation. |  | Identify cause and clean, repair, or replace as necessary. |
| 16 | Inspect all burner gaskets. |  | Replace any gaskets that are damaged or would fail to seal adequately. |
| 17 | Inspect retention head, electrodes and ceramic insulation. |  | Clean retention head, electrodes and ceramic insulation of soot and carbon. Change electrodes with ceramic cracks or if tips are rounded. |
| 18 | Inspect electrodes for proper positioning. |  | Position electrodes as necessary. |
| 19 | Measure and record photo-cell (cad cell) resistance. |  | Remove photo-cell (cad cell), check resistance, and clean as necessary. Ensure resistance is within OEM specifications. |
| 20 | Verify proper combustion air volume or provisions. |  | Ensure air volume is correct per OEM instructions and local code. Remove lint or other foreign material around burner combustion air openings that may obstruct airflow. |
| 21 | Verify burner head or nozzle type and location per OEM’s specifications. |  | Adjust as necessary. |
| 22 | Replace oil burner nozzle. |  | Install new (never attempt cleaning) identical flow rated nozzle (verify gallons per hour, spray angle and pattern). |
| 23 | Replace fuel filter. |  | Replace filter. |
| 24 | Test burner motor and blower assembly for correct operation. |  | Correct as needed. |
| 25 | Bleed oil line. |  | With open fuel supply (cap removed), on a one-pipe system, remove any air from oil line. |
| 26 | Measure and record oil pressure. |  | Adjust oil pressure as needed, per OEM specification. |
| 27 | Inspect oil pump and connections for leaks. |  | Repair leaks as needed. |
| 28 | On a two line/pipe oil system verify that oil is returning to tank. |  | Adjust as needed per OEM specifications. |
| 29 | Measure and record ignition transformer secondary voltage. |  | Nominal range is 10,000 V ac for iron core transformers. Solid state igniters cannot be tested with an iron core transformer tester. |
| 30 | Perform combustion analysis test. Measure and record test results. |  | Adjust as needed. |
| 31 | Measure and record TD across heat exchanger. |  | Verify with furnace rating plate, adjust airflow until TD is within OEM’s rating. |
| 32 | Check primary burner control safety timing. |  | Replace safety control if timing exceeds OEM’s specifications. |
| 33 | Inspect vent exhaust system (e.g., chimney, chimney liner, flue, L-vent and exhaust vent) for signs of improper condensation, water, corrosion, cracks, fractures, and blockages. |  | Clean, remove blockages, repair, or replace as necessary. |
| 34 | Inspect all vent or chimney connectors for rust discoloration, or signs of condensate. |  | Repair or replace as necessary. |
| 35 | Inspect inlet and exhaust vent pipe for proper support, slope, and termination. Ensure they are securely fastened. |  | Repair or replace as necessary. |
| 36 | Inspect for combustible materials placed too close to vent or pipe. |  | Relocate to safe place or provide approved clearance reduction. |
| Closure of the job |  |  |  |
| 37 | Clean the workspace Collect all tools and material |  | Not applicable |
| 38 | Ask feedback on the job to the customer Report the feedback in the customer feedback tool |  | Not applicable |

# Electric Furnace Inspection Checklist

| # | Inspection Task | Recommended Corrective Actions |
| --- | --- | --- |
| Cabinet |  |  |
| 1 | Inspect cabinet, cabinet fasteners, and cabinet panels. | Repair or replace insulation to ensure proper operation. Replace lost fasteners as needed to ensure proper integrity and fit/finish of equipment (as applicable). Seal air leaks. |
| 2 | Inspect the required clearance (e.g., service) around cabinet. | Record and report instances where the cabinet does not meet the requirements. |
| Electrical |  |  |
| 3 | Inspect electrical disconnect box. | Ensure electrical connections are clean and tight. Ensure fused disconnects use the proper fuse size and are not bypassed. Ensure case is intact and complete. Replace as necessary. |
| 4 | Ensure proper equipment grounding. | Tighten, correct and repair as necessary. |
| 5 | Measure and record line voltage. | Compare to OEM specifications or equipment nameplate data. Notify homeowner and/or utility. |
| 6 | Inspect and test contactors and relays. | Look for pitting or other signs of damage. Replace contactors and relays demonstrating evidence of excessive contact arcing and pitting. |
| 7 | Inspect electrical connections and wire. | Ensure wire size and type match the load conditions. Tighten all loose connections, replace heat discolored connections, and repair or replace any damaged electrical wiring. |
| 8 | Inspect motor capacitors. | Replace those that are bulged, split, incorrectly sized, or do not meet OEM specifications. |
| 9 | Measure and record amperage draw to motor/nameplate data (FLA) as available. | If outside OEM rating or specification, inspect for cause and repair as necessary. |
| 10 | Test electric heater’s capacity and sequence of operation. | If outside OEM rating or sequencer specification, inspect for cause and repair as necessary. |
| Blower Assembly |  |  |
| 11 | Determine and record airflow across heating elements. | Verify all grilles, registers, and balancing dampers are open and free of obstruction. Adjust, clean, replace, and repair as necessary to ensure to proper airflow. |
| 12 | Test variable frequency drive (e.g., ECM) for proper operation. | Replace if necessary to ensure proper operation. |
| 13 | Inspect fan belt tension. Inspect belt and pulleys for wear and tear. | Repair or replace as necessary to ensure proper operation (if applicable). |
| 14 | Confirm the fan blade or blower wheel has a tight connection to the blower motor shaft. Inspect fan for free rotation and minimal endplay. Measure and record amp draw. | Lubricate bearings as needed, only if recommended by OEM. If amp draw exceeds OEM specifications then adjust motor speed or otherwise remedy the cause. If due to motor failure recommend replacement of blower motor. |
| Closure of the job |  |  |
| 15 | Clean the workspace Collect all tools and material | Not applicable |
| 16 | Ask feedback on the job to the customer Report the feedback in the customer feedback tool | Not applicable |

# Evaporator Coil inspection checklist

| # |  | Inspection Task | Recommended Corrective Actions |
| --- | --- | --- | --- |
| Cabinet |  |  |  |
| 1 | Inspect cabinet, cabinet fasteners, and cabinet panels. |  | Repair or replace insulation to ensure proper operation. Replace lost fasteners as needed to ensure proper integrity and fit/finish of equipment (as applicable). Seal air leaks.* |
| 2 | Inspect the required clearance (e.g., service) around cabinet. Ensure no obstacles to airflow have been installed that would impede airflow. |  | Record and report instances where the cabinet does not meet the requirements. |
| Condensate Removal |  |  |  |
| 3 | Inspect condensate drain piping (and traps) for proper operation. |  | Clean, insulate, repair, or replace as necessary. |
| 4 | Inspect for condensate blowing from coil into cabinet or air distribution system.* |  | Adjust fan speed, clean coil fins, ensure OEM supplied deflectors are in place, or replace coil as necessary to eliminate water carry over. |
| 5 | Inspect drain pan and accessible drain line for biological growth. |  | Clean as needed to remove bio growth and ensure proper operation, add algae tablets or strips as necessary. Ensure algae tablets and cleaning agent are compatible with the fin and tube material. |
| 6 | Inspect secondary drain lines, drain pans, and overflow protection devices, as applicable, for proper drain flow and evidence of water in secondary drain pan.* |  | Remove any blockages and investigate cause of recent water in drain pan. |
| Refrigeration |  |  |  |
| 7 | Confirm correct airflow using delta- T and/or static pressure, and compare to OEM target. |  | Adjust the system for proper airflow. |
| 8 | Measure and record dry bulb and wet bulb TD across evaporator coil.5* |  | If DB and/or WB values are outside of appropriate OEM ranges, check for correct airflow, refrigerant charge, and operating conditions. |
| 9 | Inspect coil fins. |  | Ensure fins are visibly clean, straight, and open. Clean and straighten as required. |
| 10 | Inspect accessible refrigerant lines, joints, components, and coils for oil leaks. |  | Test all oil stained joints for leaks, clean or repair as necessary. |
| 11 | Inspect refrigerant line insulation. |  | Repair or replace refrigerant line insulation. |
| 12 | Measure pressure drop across the coil. |  | Adjust, clean, replace, and repair as necessary to ensure to proper airflow. |
| Does not apply to wall- or ceiling mounted evaporator units matched with a ductless mini split. |  |  |  |
| Closure of the job |  |  |  |
| 13 | Clean the workspace Collect all tools and material |  | Not applicable |
| 14 | Ask feedback on the job to the customer Report the feedback in the customer feedback tool |  | Not applicable |

# Condenser Unit Inspection Checklist

| # | Inspection Task | Recommended Corrective Actions |
| --- | --- | --- |
| Cabinet |  |  |
| 1 | Inspect cabinet, cabinet fasteners, and cabinet panels. | Repair or replace insulation to ensure proper operation. Replace lost fasteners as needed to ensure proper integrity and fit/finish of equipment (as applicable). Seal air leaks.* |
| 2 | Inspect the required clearance (e.g., service) around cabinet. | Record and report instances where the cabinet does not meet the requirements. |
| Electrical |  |  |
| 3 | Inspect electrical disconnect box. | Ensure electrical connections are clean and tight. Ensure fused disconnects use the proper fuse size and are not bypassed. Ensure the case is intact and complete. Replace as necessary. |
| 4 | Ensure proper equipment grounding. | Tighten, correct and repair as necessary. |
| 5 | Measure and record line voltage. | Compare to OEM specifications or equipment nameplate data. Notify homeowner and/or utility. |
| 6 | Inspect and test contactors and relays. | Look for pitting or other signs of damage. Replace contactors and relays demonstrating evidence of excessive contact arcing and pitting. |
| 7 | If accessible, check printed circuit for hot spots and other damage. | Replace as necessary. |
| 8 | Inspect electrical connections and wire. | Ensure wire size and type match the load conditions. Tighten all loose connections, replace heat discolored connections, and repair or replace any damaged electrical wiring. |
| 9 | Inspect motor capacitors. | Replace those that are bulged, split, incorrectly sized, or do not meet OEM specifications. |
| 10 | Measure and record amperage draw to motor/nameplate data (FLA) as available. | If outside OEM rating or specification, inspect for cause and repair as necessary. |
| Refrigeration |  |  |
| 11 | Inspect accessible refrigerant lines, joints, components, and coils for oil leaks. | Test all oil stained joints for leaks, clean or repair as necessary. |
| 12 | If indoor airflow is within OEM specifications but TD is not (see Checklist 5.7 #h), check refrigerant charge using manufacturer recommended procedure.6 | Adjust charge as necessary7. |
| 13 | Inspect refrigerant line insulation. | Repair or replace refrigerant line insulation. |
| Condenser Fan Motor |  |  |
| 14 | Confirm the fan blade or blower wheel has a tight connection to the blower motor shaft. Inspect fan for free rotation and minimal endplay. Measure and record amp draw. | Lubricate bearings as needed, only if recommended by OEM. If amp draw exceeds OEM specifications then adjust motor speed or otherwise remedy the cause. If due to motor failure recommend replacement of blower motor. |
| Condenser Coil |  |  |
| 15 | Inspect coil fins. | Clean, straighten, and repair as required. |
| HP Additional Tasks for Air-to-Air Heat Pump Condensers |  |  |
| 16 | Test reversing valve operation. | Record findings, repair replace as necessary. |
| 17 | If indoor airflow is within OEM specifications but TD is not, check refrigerant charge using manufacturer recommended procedure.8 | Adjust charge as necessary9. |
| 18 | Test defrost cycle controls. | Repair, replace or adjust controls as needed. |
| 19 | Inspect outdoor unit condensate drain ports. | Ensure condensate drain ports are open and the unit is elevated above obstructions to allow free flow of condensate or per local code for seasonal obstructions like snow. |
| Closure of the job |  |  |
| 20 | Clean the workspace Collect all tools and material | Not applicable |
| 21 | Ask feedback on the job to the customer Report the feedback in the customer feedback tool | Not applicable |

# Fan Coil Inspection Checklist

| # | Inspection Task | Recommended Corrective Actions |
| --- | --- | --- |
| Cabinet |  |  |
| 1 | Inspect cabinet, cabinet fasteners, and cabinet panels. | Repair or replace insulation to ensure proper operation. Replace lost fasteners as needed to ensure proper integrity and fit/finish of equipment (as applicable). Seal air leaks. |
| 2 | Inspect the required clearance (e.g., service) around cabinet. | Record and report instances where the cabinet does not meet the requirements. |
| Electrical |  |  |
| 3 | Inspect electrical disconnect box. | Ensure electrical connections are clean and tight. Ensure fused disconnects use the proper fuse size and are not bypassed. Ensure case is intact and complete. Replace as necessary. |
| 4 | Ensure proper equipment grounding. | Tighten, correct and repair as necessary. |
| 5 | Measure and record line voltage. | Compare to OEM specifications or equipment nameplate data. Notify homeowner and/or utility. |
| 6 | Inspect and test contactors and relays. | Look for pitting or other signs of damage. Replace contactors and relays demonstrating evidence of excessive contact arcing and pitting. |
| 7 | Inspect electrical connections and wire. | Ensure wire size and type match the load conditions. Tighten all loose connections, replace heat discolored connections, and repair or replace any damaged electrical wiring. |
| 8 | Inspect motor capacitors. | Replace those that are bulged, split, incorrectly sized, or do not meet OEM specifications. |
| 9 | Measure and record amperage draw to motor/nameplate data (FLA) as available. | If outside OEM rating or specification, inspect for cause and repair as necessary. |
| Blower Assembly |  |  |
| 10 | Determine and record airflow across heat exchanger/coil. | Verify all grilles, registers, and balancing dampers are open and free of obstruction and operating properly. Adjust, clean, replace, and repair as necessary to ensure to proper airflow. |
| 11 | Test variable frequency drive (e.g., ECM) for proper operation. | Replace if necessary to ensure proper operation. |
| 12 | Inspect fan belt tension. Inspect belt and pulleys for wear and tear. | Repair or replace as necessary to ensure proper operation (if applicable). |
| 13 | Confirm the fan blade or blower wheel has a tight connection to the blower motor shaft. Inspect fan for free rotation and minimal endplay. Measure and record amp draw. | Lubricate bearings as needed, only if recommended by OEM. If amp draw exceeds OEM specifications then adjust motor speed or otherwise remedy the cause. If due to motor failure recommend replacement of blower motor. |
| Evaporator Coil |  |  |
| 14 | Inspect coil, refrigeration components, fittings and fins. | Check for signs of refrigerant leaks. Ensure fins are clean, straight, and open. Clean and straighten as required. |
| 15 | Confirm correct airflow using delta- T and/or static pressure, and compare to OEM target. | Adjust the system for proper airflow. |
| 16 | Measure and record dry bulb and wet bulb TD across evaporator coil. | If DB and/or WB values are outside of appropriate OEM ranges, check for correct airflow, refrigerant charge, and operating conditions. |
| 17 | Inspect refrigerant line insulation. | Repair or replace refrigerant line insulation. |
| Condensate removal |  |  |
| 18 | Inspect for condensate blowing from coil into cabinet or air distribution system. | Adjust fan speed, clean coil fins, ensure OEM supplied deflectors are in place, or replace coil as necessary to eliminate water carry over. |
| 19 | Inspect condensate drain piping (and traps) for proper operation. | Clean, insulate, repair, or replace as necessary. |
| 20 | Inspect drain pan and accessible drain line for biological growth. | Clean as needed to remove bio growth and ensure proper operation, add algae tablets or strips as necessary. Ensure algae tablets and cleaning agent are compatible with the fin and tube material. |
| Auxiliary or Supplemental Electric Heaters |  |  |
| 21 | Test electric heater’s capacity and sequence of operation. | If outside OEM rating or sequencer specification, inspect for cause and repair as necessary. |
| Closure of the job |  |  |
| 22 | Clean the workspace Collect all tools and material | Not applicable |
| 23 | Ask feedback on the job to the customer Report the feedback in the customer feedback tool | Not applicable |

# Gas Boiler System Inspection Checklist

| # | Inspection Task | Recommended Corrective Actions |
| --- | --- | --- |
| Cabinet |  |  |
| 1 | Inspect cabinet, cabinet fasteners, and cabinet panels. | Repair or replace insulation to ensure proper operation. Replace lost fasteners as needed to ensure proper integrity and fit/finish of equipment (as applicable). |
| 2 | Inspect the required clearance (e.g., combustion and service) around cabinet. | Record and report instances where the cabinet does not meet the requirements. |
| Electrical |  |  |
| 3 | Inspect electrical disconnect box. | Ensure electrical connections are clean and tight. Ensure fused disconnects use the proper fuse size and are not bypassed. Ensure case is intact and complete. Replace as necessary. |
| 4 | Ensure proper equipment grounding. | Tighten, correct and repair as necessary. |
| 5 | Measure and record line voltage. | Compare to OEM specifications or equipment nameplate data. Notify homeowner and/or utility. |
| 6 | Inspect and test contactors and relays. | Look for pitting or other signs of damage. Replace contactors and relays demonstrating evidence of excessive contact arcing and pitting. |
| 7 | Inspect electrical connections and wire. | Ensure wire size and type match the load conditions. Tighten all loose connections, replace heat discolored connections, and repair or replace any damaged electrical wiring. |
| 8 | Inspect motor capacitors. | Replace those that are bulged, split, incorrectly sized, or do not meet OEM specifications. |
| 9 | Measure and record amperage draw to motor/nameplate data (FLA) as available. | If outside OEM rating or specification, inspect for cause and repair as necessary. |
| Gas Combustion |  |  |
| 10 | Inspect combustion chamber, burner and flue. | Look for signs of water, corrosion, and blockage. |
| 11 | Inspect heat exchanger for signs of corrosion, fouling, structural problems (e.g., cracks, perforations, and bulges), and erratic flame operation during blower operation. | Clean or replace as needed. |
| 12 | Visually inspect burners for signs of contamination. | Clean, repair or replace as necessary. |
| 13 | Inspect the burner blower wheel | Clean as needed to ensure proper operation. |
| 14 | Inspect hot surface igniter for cracks (white spots when energized or check cold with ohmmeter and proper supply voltage). | Replace if outside OEM’s specifications. |
| 15 | Measure and record inlet gas pressure at inlet pressure tap. | If the inlet gas pressure is insufficient for OEM operation specifications, contact the gas supplier. |
| 16 | Measure, record, and adjust manifold pressure as necessary. | Adjust the gas valve to provide proper manifold pressure. |
| 17 | Test main burner ignition. | Replace thermocouple or flame sensor/pilot assembly if outside of OEM recommended operational range under load. |
| 18 | Test burners. | Fire unit and adjust air shutters (if used) for OEM specification compliance. |
| 19 | Test inducer fan motor and blower assembly. | Correct as needed. |
| 20 | Ensure combustion air volume is correct. | Ensure air volume is correct per local code. |
| 21 | Perform combustion analysis test. Measure and record test results. | Adjust as needed. |
| 22 | Measure and record TD across the heat exchanger. | Clean components or adjust water flow as necessary to meet necessary operating conditions and design parameters. |
| Hydronic Loop |  |  |
| 23 | Inspect screen on reducing valve, pressure reducing valve, and “Y” strainer if available. | Clean or replace as necessary. |
| 24 | Test bladder expansion tank for proper air cushion or proper air cushion on expansion tank. | Adjust to provide proper air cushion on expansion tank as per manufactures specifications. |
| 25 | Inspect water pump. | Clean or clear as needed to reduce cavitation and ensure proper operation. |
| 26 | Measure and record TD of water entering to water leaving coil/ heat exchanger. | Adjust flow rate as necessary. |
| 27 | Measure and record PD of the water loop across the water heat exchanger. | Adjust water pump or control valve as necessary. |
| Venting |  |  |
| 28 | Inspect inside of chimney/ flue/ inlet and exhaust vent for water, signs of condensation, corrosion, cracks, fractures, and blockages. | Clean, remove blockages, repair, or replace as necessary. |
| 29 | Inspect all vent connectors for rust discoloration, or signs of condensate. | Ensure they are securely fastened. Repair or replace as necessary. |
| 30 | Inspect inlet and exhaust vent pipe for proper support, slope, and termination. | Repair or replace as necessary. |
| 31 | Inspect for combustible materials placed too close to vent or pipe. | Relocate to safe place or provide approved clearance reduction. |
| Closure of the job |  |  |
| 32 | Clean the workspace Collect all tools and material | Not applicable |
| 33 | Ask feedback on the job to the customer Report the feedback in the customer feedback tool | Not applicable |

# Oil Boiler System Inspection Checklist

| # | Inspection Task | Recommended Corrective Actions |  |
| --- | --- | --- | --- |
| Cabinet |  |  |  |
| 1 | Inspect cabinet, cabinet fasteners, and cabinet panels. |  | Repair or replace insulation to ensure proper operation. Replace lost fasteners as needed to ensure proper integrity and fit/finish of equipment (as applicable). |
| 2 | Inspect the required clearance (e.g., combustion and service) around cabinet. |  | Record and report instances where the cabinet does not meet the requirements. |
| Electrical |  |  |  |
| 3 | Inspect electrical disconnect box. |  | Ensure electrical connections are clean and tight. Ensure fused disconnects use the proper fuse size and are not bypassed. Ensure case is intact and complete. Replace as necessary. |
| 4 | Ensure proper equipment grounding. |  | Tighten, correct and repair as necessary. |
| 5 | Measure and record line voltage. |  | Compare to OEM specifications or equipment nameplate data. Notify homeowner and/or utility. |
| 6 | Inspect and test contactors and relays. |  | Look for pitting or other signs of damage. Replace contactors and relays demonstrating evidence of excessive contact arcing and pitting. |
| 7 | Inspect electrical connections and wire. |  | Ensure wire size and type match the load conditions. Tighten all loose connections, replace heat discolored connections, and repair or replace any damaged electrical wiring. |
| 8 | Inspect motor capacitors. |  | Replace those that are bulged, split, incorrectly sized, or do not meet OEM specifications. |
| 9 | Measure and record amperage draw to motor/nameplate data (FLA) as available. |  | If outside OEM rating or specification, inspect for cause and repair as necessary. |
| Oil Combustion |  |  |  |
| 10 | Inspect combustion chamber for structural problems (e.g., cracks, perforations, and bulges). |  | Identify cause and clean, repair, or replace as necessary. |
| 11 | Inspect heat exchanger and internal flue for signs of corrosion, fouling, structural problems (e.g., cracks, perforations, and bulges), and erratic flame operation during blower operation. |  | Identify cause and clean, repair, or replace as necessary. |
| 12 | Inspect all burner gaskets. |  | Replace any gaskets that are damaged or would fail to seal adequately. |
| 13 | Inspect retention head, electrodes and ceramic insulation. |  | Clean retention head, electrodes and ceramic insulation of soot and carbon. Change electrodes with ceramic cracks or if tips are rounded. |
| 14 | Inspect electrodes for proper positioning. |  | Position electrodes as necessary. |
| 15 | Measure and record photo-cell (cad cell) resistance. |  | Remove photo-cell (cad cell), check resistance, and clean as necessary. Ensure resistance is within OEM specifications. |
| 16 | Clean combustion air inlet. |  | Remove lint or other foreign material around burner combustion air openings that may obstruct airflow. |
| 17 | Verify burner head or nozzle type and location per OEM’s specifications. |  | Make all adjustments as necessary. |
| 18 | Replace oil burner nozzle. |  | Install new (never attempt cleaning) identical flow rated nozzle (verify gallons per hour, spray angle and pattern). |
| 19 | Replace fuel filter. |  | Replace filter. |
| 20 | Test inducer fan motor and blower assembly. |  | Correct as needed. |
| 21 | Bleed oil line. |  | With open fuel supply (cap removed), on a one-pipe system, remove any air from oil line. |
| 22 | Measure, adjust, and record oil pressure. |  | Measure and adjust oil pressure. |
| 23 | Inspect oil pump for proper pressure and leaks. |  | If pump pressure is below OEM specifications or there are signs of leaks, remove oil pump cover and gasket. Discard gasket. With fine-bristle brush and solvent, then clean strainer or replace. Reassemble with new gasket. Retest pump. |
| 24 | Test fuel pump for proper operation, pressure, and cut-off. Measure and record line vacuum. |  | Install a pressure gauge in the nozzle port and run the burner to observe operating pressure and record. Shut the burner off and record cut-off pressure. If the cut-off pressure drops below OEM specifications replace pump or add check valve. |
| 25 | Measure and record ignition transformer secondary voltage. |  | Nominal range is 10,000 V ac for iron core transformers. Solid state igniters cannot be tested with an iron core transformer tester. |
| 26 | Ensure combustion air volume is correct. |  | Ensure air volume is correct per local code. |
| 27 | Perform combustion analysis test. Measure and record test results. |  | Adjust as needed. |
| 28 | Measure and record TD across heat exchanger. |  | Verify with furnace rating plate. If TD is outside OEM’s rating, identify cause and then clean, repair, or replace as necessary. |
| 29 | Check primary control safety timing. |  | Disconnect the cad cell and run the burner and time the lockout. Replace safety control if timing exceeds OEM’s specifications. |
| Hydronic Loop |  |  |  |
| 30 | Inspect screen on reducing valve, pressure reducing valve, and “Y” strainer if available. |  | Clean or replace as necessary. |
| 31 | Test bladder/expansion tank for proper air cushion or proper air cushion on expansion tank. |  | Adjust to provide proper air cushion on expansion tank as per manufactures specifications. |
| 32 | Inspect water pump. |  | Clean or clear as needed to reduce cavitation and ensure proper operation. |
| 33 | Measure and record PD of the water loop across the refrigerant water heat exchanger. |  | Adjust water pump or control valve as necessary. |
| 34 | Measure and record TD of water entering to water leaving coil/ heat exchanger. |  | If TD is outside OEM’s specifications, identify cause and then clean, repair, or replace as necessary. |
| 35 | Inspect auto air vent and check for air in system. |  | Clean or replace air vents as necessary. |
| Venting |  |  |  |
| 36 | Inspect inside of chimney/ flue/ inlet and exhaust vent for water, signs of condensation, corrosion, cracks, fractures, and blockages. |  | Clean, remove blockages, repair, or replace as necessary. |
| 37 | Inspect all vent connectors for rust discoloration, or signs of condensate. |  | Ensure they are securely fastened. Repair or replace as necessary. |
| 38 | Inspect inlet and exhaust vent pipe for proper support, slope, and termination. |  | Repair or replace as necessary. |
| 39 | Inspect for combustible materials placed too close to vent or pipe. |  | Relocate to safe place or provide approved clearance reduction. |
| Closure of the job |  |  |  |
| 40 | Clean the workspace Collect all tools and material |  | Not applicable |
| 41 | Ask feedback on the job to the customer Report the feedback in the customer feedback tool |  | Not applicable |

# Electric Boiler System Inspection Checklist

| # | Inspection Task | Recommended Corrective Actions |
| --- | --- | --- |
| Cabinet |  |  |
| 1. | Inspect cabinet, cabinet fasteners, and cabinet panels. | Repair or replace insulation to ensure proper operation. Replace lost fasteners as needed to ensure proper integrity and fit/finish of equipment (as applicable). Seal air leaks. |
| 2 | Inspect the required clearance (e.g., service) around cabinet. | Record and report instances where the cabinet does not meet the requirements. |
| Electrical |  |  |
| 3 | Inspect electrical disconnect box. | Ensure electrical connections are clean and tight. Ensure fused disconnects use the proper fuse size and are not bypassed. Ensure case is intact and complete. Replace as necessary. |
| 4 | Ensure proper equipment grounding. | Tighten, correct and repair as necessary. |
| 5 | Measure and record line voltage. | Compare to OEM specifications or equipment nameplate data. Notify homeowner and/or utility. |
| 6 | Inspect and test contactors and relays. | Look for pitting or other signs of damage. Replace contactors and relays demonstrating evidence of excessive contact arcing and pitting. |
| 7 | Inspect electrical connections and wire. | Ensure wire size and type match the load conditions. Tighten all loose connections, replace heat discolored connections, and repair or replace any damaged electrical wiring. |
| 8 | Inspect motor capacitors. | Replace those that are bulged, split, incorrectly sized, or do not meet OEM specifications. |
| 9 | Measure and record amperage draw to motor/nameplate data (FLA) as available. | If outside OEM rating or specification, inspect for cause and repair as necessary. |
| Electric Water Heating |  |  |
| 10 | Measure and record TD of water entering to water leaving heat exchanger. | If outside OEM rating or specification, inspect for cause and repair as necessary. |
| 11 | Test electric heater’s capacity and sequence of operation. | If outside OEM rating or sequencer specification, inspect for cause and repair as necessary. |
| Hydronic Loop |  |  |
| 12 | Inspect screen on reducing valve, pressure reducing valve, and “Y” strainer if available. | Clean or replace as necessary. |
| 13 | Test bladder expansion tank for proper air cushion or proper air cushion on expansion tank. | Adjust to provide proper air cushion on expansion tank as per manufactures specifications. |
| 14 | Inspect water pump. | Clean or clear as needed to reduce cavitation and ensure proper operation. |
| 15 | Measure and record TD of water entering to water leaving coil/ heat exchanger. | Add or remove refrigerant or adjust firing rate as necessary. |
| 16 | Measure and record PD of the water loop across the refrigerant water heat exchanger. | Adjust water pump or control valve as necessary. |
| Closure of the job |  |  |
| 17 | Clean the workspace Collect all tools and material | Not applicable |
| 18 | Ask feedback on the job to the customer Report the feedback in the customer feedback tool | Not applicable |

# Package Units

| # | Inspection Task | Recommended Corrective Actions |
| --- | --- | --- |
| Cabinet |  |  |
| 1 | Inspect cabinet, cabinet fasteners, and cabinet panels. | Repair or replace insulation to ensure proper operation. Replace lost fasteners as needed to ensure proper integrity and fit/finish of equipment (as applicable). Seal air leaks on indoor air processing sections. |
| 2 | Inspect the required clearance (e.g., combustion and service) around cabinet. | Record and report instances where the cabinet does not meet the requirements. |
| Electrical |  |  |
| 3 | Inspect electrical disconnect box. | Ensure electrical connections are clean and tight. Ensure fused disconnects use the proper fuse size and are not bypassed. Ensure case is intact and complete. Replace as necessary. |
| 4 | Ensure proper equipment grounding. | Tighten, correct and repair as necessary. |
| 5 | Measure and record line voltage. | Compare to OEM specifications or equipment nameplate data. Notify homeowner and/or utility. |
| 6 | Inspect and test contactors and relays. | Look for pitting or other signs of damage. Replace contactors and relays demonstrating evidence of excessive contact arcing and pitting. |
| 7 | Inspect electrical connections and wire. | Ensure wire size and type match the load conditions. Tighten all loose connections, replace heat discolored connections, and repair or replace any damaged electrical wiring. |
| 8 | Inspect motor capacitors. | Replace those that are bulged, split, incorrectly sized, or do not meet OEM specifications. |
| 9 | Measure and record amperage draw to motor/nameplate data (FLA) as available. | If outside OEM rating or specification, inspect for cause and repair as necessary. |
| Indoor Blower Motor |  |  |
| 10 | Determine and record airflow across heat exchanger/coil. | Verify all grilles, registers, and balancing dampers are open and free of obstruction and operating properly. Adjust, clean, replace, and repair as necessary to ensure to proper airflow. |
| 11 | Test variable frequency drive (e.g., ECM) for proper operation. | Replace if necessary to ensure proper operation. |
| 12 | Inspect fan belt tension. Inspect belt and pulleys for wear and tear. | Repair or replace as necessary to ensure proper operation (if applicable). |
| 13 | Confirm the fan blade or blower wheel has a tight connection to the blower motor shaft. Inspect fan for free rotation and minimal endplay. Measure and record amp draw. | Lubricate bearings as needed, only if recommended by OEM. If amp draw exceeds OEM specifications then adjust motor speed or otherwise remedy the cause. If due to motor failure recommend replacement of blower motor. |
| Evaporator Coil Section |  |  |
| 14 | Inspect coil fins. | Ensure fins are clean, straight, and open. Clean and straighten as required. |
| 15 | Inspect for condensate blowing from coil into cabinet or air distribution system. | Adjust fan speed, clean coil fins, or replace coil as necessary to eliminate water carry over. |
| 16 | Inspect accessible refrigerant connecting lines, joints, and coils for oil leaks. | Test all oil stained joints for leaks, clean or repair as necessary. |
| 17 | Confirm correct airflow using delta- T and/or static pressure, and compare to OEM target. | Adjust the system for proper airflow. |
| 18 | Measure and record dry bulb and wet bulb TD across evaporator coil10. | If DB and/or WB values are outside of appropriate OEM ranges, check for correct airflow, refrigerant charge, and operating conditions |
| Condensate removal |  |  |
| 19 | Inspect for condensate blowing from coil into cabinet or air distribution system. | Adjust fan speed, clean coil fins, ensure OEM supplied deflectors are in place, or replace coil as necessary to eliminate water carry over. |
| 20 | Inspect condensate drains (and traps) for proper operation. | Clean, insulate, repair, or replace as necessary. |
| 21 | Inspect drain pan and accessible drain line for biological growth. | Clean as needed to remove bio growth and ensure proper operation, add algae tablets or strips as necessary. Ensure algae tablets and cleaning agent are compatible with the fin and tube material. |
| Condenser Blower Motor |  |  |
| 22 | Confirm the fan blade or blower wheel has a tight connection to the blower motor shaft. Inspect fan for free rotation and minimal endplay. Measure and record amp draw. | Lubricate bearings as needed, only if recommended by OEM. If amp draw exceeds OEM specifications then adjust motor speed or otherwise remedy the cause. If due to motor failure recommend replacement of blower motor. |
| Condenser Coil Section |  |  |
| 23 | Inspect coil fins. | Ensure fins are clean, straight, and open. Clean and straighten as required. |
| 24 | Inspect accessible refrigerant connecting lines, joints, and coils for oil leaks. | Test all oil stained joints for leaks, clean or repair as necessary. |
| Refrigeration |  |  |
| 25 | Inspect accessible refrigerant connecting lines, joints, and coils for oil leaks. | Test all oil stains for leaks, clean or repair as necessary. |
| 26 | If indoor airflow is within OEM specifications but TD is not, check refrigerant charge using manufacturer recommended procedure (good diagnostic field practice is to measure superheat or sub-cooling to ensure proper refrigerant charge) | Adjust charge as necessary. Ensure that the metering device (and sensing bulb) is properly installed |
| Auxiliary or Supplemental Electric Heaters |  |  |
| 27 | Test electric heater’s capacity and sequence of operation. | If outside OEM rating or sequencer specification, inspect for cause and repair as necessary. |
| Additional Tasks for Package Heat Pumps |  |  |
| 28 | Test reversing valve operation. | Record findings, repair replace as necessary. |
| 29 | If indoor airflow is within OEM specifications but TD is not, check refrigerant charge using manufacturer recommended procedure.13 | Adjust charge as necessary14. |
| 30 | Test defrost cycle controls. | Repair, replace or adjust controls as needed. |
| 31 | Inspect condenser section condensate drain ports. | Ensure condensate drain ports are open and elevated above obstructions to allow free flow of condensate or per local code for seasonal obstructions like snow. |
| Gas Combustion |  |  |
| 32 | Inspect combustion chamber, burner and flue. | Look for signs of water, corrosion, and blockage. |
| 33 | Inspect heat exchanger for signs of corrosion, fouling, structural problems (e.g., cracks, perforations, and bulges), and erratic flame operation during blower operation. | Clean or replace as needed. |
| 34 | Visually inspect burners for signs of contamination. | Clean, repair or replace as necessary. |
| 35 | Inspect the burner blower wheel | Clean as needed to ensure proper operation. |
| 36 | Inspect hot surface igniter for cracks (white spots when energized or check cold with ohmmeter and proper supply voltage). | Replace if outside OEM’s specifications. |
| 37 | Measure and record inlet gas pressure at inlet pressure tap. | If the inlet gas pressure is insufficient for OEM operation specifications, contact the gas supplier. |
| 38 | Measure, record, and adjust manifold pressure as necessary. | Adjust the gas valve to provide proper manifold pressure. |
| 39 | Test main burner ignition. | Clean thermocouple or flame sensor/pilot assembly. |
| 40 | Test burners. | Fire unit and adjust air shutters (if used) for OEM specification compliance. |
| 41 | Test inducer fan motor and blower assembly. | Correct as needed. |
| 42 | Ensure combustion air volume is correct. | Ensure air volume is correct per local code. |
| 43 | Perform combustion analysis test. Measure and record test results. | Adjust as needed. |
| 44 | Measure and record TD across the heat exchanger. | Clean components or adjust airflow as necessary to meet necessary operating conditions and design parameters. |
| Venting |  |  |
| 45 | Inspect vent termination for water, signs of condensation, corrosion, cracks, fractures, and blockages. | Clean, remove blockages, repair, or replace as necessary. |
| 46 | Inspect all vent connectors for rust discoloration, or signs of condensate. | Ensure they are securely fastened. Repair or replace as necessary. |
| 47 | Inspect inlet and exhaust vent pipe for proper support, slope, and termination. | Repair or replace as necessary. |
| 48 | Inspect for combustible materials placed too close to vent or pipe. | Relocate to safe place. |
| Closure of the job |  |  |
| 49 | Clean the workspace Collect all tools and material | Not applicable |
| 50 | Ask feedback on the job to the customer Report the feedback in the customer feedback tool | Not applicable |

# Geothermal/ Water Source Heat Pumps

# Evaporative Coolers

| # | Inspection Task | Recommended Corrective Actions |
| --- | --- | --- |
| Cabinet |  |  |
| 1 | Inspect cabinet, cabinet fasteners, and cabinet panels. | Repair or replace insulation to ensure proper operation. Replace lost fasteners as needed to ensure proper integrity and fit/finish of equipment (as applicable). Seal air leaks. |
| 2 | Inspect the required clearance (e.g., service) around cabinet. | Record and report instances where the cabinet does not meet the requirements. |
| Electrical |  |  |
| 3 | Inspect electrical disconnect box. | Ensure electrical connections are clean and tight. Ensure fused disconnects use the proper fuse size and are not bypassed. Ensure case is intact and complete. Replace as necessary. |
| 4 | Ensure proper equipment grounding. | Tighten, correct and repair as necessary. |
| 5 | Measure and record line voltage. | Compare to OEM specifications or equipment nameplate data. Notify homeowner and/or utility. |
| 6 | Inspect and test contactors and relays. | Look for pitting or other signs of damage. Replace contactors and relays demonstrating evidence of excessive contact arcing and pitting. |
| 7 | Inspect electrical connections and wire. | Ensure wire size and type match the load conditions. Tighten all loose connections, replace heat discolored connections, and repair or replace any damaged electrical wiring. |
| 8 | Inspect motor capacitors. | Replace those that are bulged, split, incorrectly sized, or do not meet OEM specifications. |
| 9 | Measure and record amperage draw to motor/nameplate data (FLA) as available. | If outside OEM rating or specification, inspect for cause and repair as necessary. |
| Blower Assembly |  |  |
| 10 | Inspect fan belt tension. Inspect belt and pulleys for wear and tear. | Repair or replace as necessary to ensure proper operation (if applicable). |
| 11 | Confirm the fan blade or blower wheel has a tight connection to the blower motor shaft. Inspect fan for free rotation and minimal endplay. Measure and record amp draw. | Lubricate bearings as needed, only if recommended by OEM. If amp draw exceeds OEM specifications then adjust motor speed or otherwise remedy the cause. If due to motor failure recommend replacement of blower motor. |
| Evaporative Cooling |  |  |
| 12 | Inspect the cooler’s bottom pan. | Clean thoroughly or repair. |
| 13 | Inspect water pump. | Clean the pump screen. Remove and foreign material from the hose adaptor. Clean other water pump components as necessary. |
| 14 | Inspect the water distributor manifold and ports. | Flush with water. Repair or replace portions of the manifold, nozzles, or fittings that do not perform per the OEM specifications. |
| 15 | Inspect the evaporative cooling media pads. | Clean scale, dirt, and foreign material from the pads. Replace pads that restrict airflow or do not perform to the OEM specifications |
| Closure of the job |  |  |
| 16 | Clean the workspace Collect all tools and material | Not applicable |
| 17 | Ask feedback on the job to the customer Report the feedback in the customer feedback tool | Not applicable |

# Accessories

| # | Inspection Task | Recommended Corrective Actions |
| --- | --- | --- |
| Common Cabinet Tasks |  |  |
| 1 | Inspect cabinet, cabinet fasteners, and cabinet panels. | Repair or replace insulation to ensure proper operation. Replace lost fasteners as needed to ensure proper integrity and fit/finish of equipment (as applicable). Clean accessible portions of cabinet interior. Seal air leaks. |
| 2 | Inspect the required clearance (e.g., combustion and service) around cabinet. | Record and report instances where the cabinet does not meet the requirements. |
| Common Electrical Tasks |  |  |
| 3 | Ensure proper equipment grounding. | Tighten, correct and repair as necessary. |
| 4 | Measure and record line voltage. | Compare to OEM specifications or equipment nameplate data. Notify homeowner and/or utility. |
| 5 | Inspect and test contactors and relays. | Look for pitting or other signs of damage. Replace contactors and relays demonstrating evidence of excessive contact arcing and pitting. |
| 6 | Inspect electrical connections and wire. | Ensure wire size and type match the load conditions. Tighten all loose connections, replace heat discolored connections, and repair or replace any damaged electrical wiring. |
| 7 | Inspect motor capacitors. | Replace those that are bulged, split, incorrectly sized, or do not meet OEM specifications. |
| 8 | Measure and record amperage draw to motor/nameplate data (FLA) as available. | If outside OEM rating or specification, inspect for cause and repair as necessary. |
| Energy and Heat Recovery Ventilators |  |  |
| 9 | Inspect filters and filter racks. | Clean filters and adjust filter racks as necessary to ensure proper fit and seal of filters per OEM’s specifications. |
| 10 | Inspect transfer core. | Wait for core to dry and clean core as necessary. |
| 11 | Inspect fresh air intake vent. | Clear and remove debris to provide to allow for proper airflow. |
| 12 | Inspect fan belt tension. Inspect belt and pulleys for wear and tear. | Repair or replace as necessary to ensure proper operation (if applicable). |
| 13 | Confirm the fan blade or blower wheel has a tight connection to the blower motor shaft. Inspect fan for free rotation and minimal endplay. Measure and record amp draw. | Lubricate bearings as needed, only if recommended by OEM. If amp draw exceeds OEM specifications then adjust motor speed or otherwise remedy the cause. If due to motor failure recommend replacement of blower motor. |
| Central System Humidifiers |  |  |
| 14 | Inspect humidifier pad. | Replace as necessary. |
| 15 | Inspect water line by gently flexing it and looking for cracks or signs of leakage. | Replace tube if it is cracked, brittle or has been damaged. |
| 16 | Inspect pad tray and frame. | Clean the tray and frame of mineral deposits as necessary. |
| 17 | Inspect drain hose and fitting. | Clean as necessary. |
| Central System Dehumidifiers |  |  |
| 18 | Inspect for particulate accumulation on filters. | Clean or replace if accumulation results in PD higher than design or airflow is outside of established operating limits. |
| 19 | Inspect air filter housing integrity and air seal. | Correct as needed. |
| 20 | Inspect condensate drain piping (and traps) for proper operation. | Clean, insulate, repair, or replace as necessary. |
| 21 | Inspect drain pan and accessible drain line for biological growth. | Clean as needed to remove bio growth and ensure proper operation, add algae tablets or strips as necessary. |
| 22 | Confirm the fan blade or blower wheel has a tight connection to the blower motor shaft. Inspect fan for free rotation and minimal endplay. Measure and record amp draw. | Lubricate bearings as needed, only if recommended by OEM. If amp draw exceeds OEM specifications then adjust motor speed or otherwise remedy the cause. If due to motor failure recommend replacement of blower motor. |
| 23 | Inspect coil fittings and fins. | Ensure fins are straight and open. Check U-Tubes for signs of refrigerant leaks. Clean and straighten as required. |
| Electronic Air Cleaners |  |  |
| 24 | Inspect for particulate accumulation on pre-filters. | Clean if accumulation results in PD higher than design or airflow is outside of established operating limits or replace if damaged or inoperable. |
| 25 | Inspect the electrodes or collector plates. | Clean as necessary. |
| Media Air Cleaners |  |  |
| 26 | Inspect for particulate accumulation pre-filters. | Replace if accumulation results in PD higher than design or airflow is outside of established operating limits or replace if damaged or inoperable. |
| Ultra-violet Lights |  |  |
| 27 | Inspect UV lamps. | Clean or replace to ensure proper operation. UV lamps may contain mercury and must be disposed of properly. Do not throw old lamps into the trash. |
| Economizers |  |  |
| 28 | Inspect inlet screen or filter for accumulation, blockage, wear and state of repair. | Clean or replace filters as necessary. |
| 29 | Inspect minimum position of outside air damper. | Adjust air damper position per design specifications or applicable codes. Repair or replace as necessary. |
| 30 | Inspect rain hood for proper attachment, security, and signs of water leakage inside the rain hood. | Repair or replace as necessary. |
| 31 | Inspect actuator motors for free range of motion. | Repair or replace as necessary. |
| Condensate Pumps |  |  |
| 32 | Test condensate pump operation and inspect condition. | Clean, flush and test for proper operation. |
| 33 | Inspect condensate drain piping (and traps) for proper operation. | Clean, insulate, repair, or replace as necessary |
| Closure of the job |  |  |
| 34 | Clean the workspace Collect all tools and material | Not applicable |
| 35 | Ask feedback on the job to the customer Report the feedback in the customer feedback tool | Not applicable |

# APPENDIX: Customer feedback tool

The customer feedback tool is an excel based database to collect and analyze customers feedback. The table below show the required data to collect

- Date of the job: 18 November 2017

- Type of the job: e.g., annual maintenance

- Customer identification: e.g., Mr Serviis

- Who delivered the service: e.g., Mr Ahmed

- Work done: e.g., replaced venting system

- Customer feedback: e.g., lack of cleaning of the work space after the work

- Action taken: e.g., instruct the employees to clean the work space, add procedure on the quality